# VSaaS Server Room - REVISED for True View Cameras

**Camera Models**: 5MP, 4MP, 2MP (realistic bitrates)

**Customers**: 25 (100 cameras total)

**Requirement**: Year-round 24/7 storage (365 days)

**Location**: India

---

## 📊 REALISTIC STORAGE CALCULATION

### **Camera Specifications & Bitrates**

| Camera | Resolution | FPS | Codec | Bitrate | Per Day | Per Year |

|--------|-----------|-----|-------|---------|---------|----------|

| **5MP** | 2560×1920 | 30 | H.264 | 6 Mbps | 64.8 GB | 23.6 TB |

| **4MP** | 2688×1520 | 30 | H.264 | 4.5 Mbps | 48.6 GB | 17.7 TB |

| **2MP** | 1920×1080 | 30 | H.264 | 3 Mbps | 32.4 GB | 11.8 TB |

**Calculation:**

```

1 Mbps = 128 KB/s

Per day (24 hrs) = 128 KB/s × 86,400 sec = 11.04 GB/Mbps

```

---

### **Your 100 Cameras Distribution**

Assume realistic mix:

- 25 × 5MP cameras = 25 × 64.8 GB/day = 1,620 GB/day

- 25 × 4MP cameras = 25 × 48.6 GB/day = 1,215 GB/day

- 50 × 2MP cameras = 50 × 32.4 GB/day = 1,620 GB/day

**Total Daily**: 1,620 + 1,215 + 1,620 = **4,455 GB/day ≈ 4.5 TB/day**

**Annual Storage (365 days)**: 4.5 × 365 = **1,642 TB ≈ 1.6 PB**

**With RAID-6 redundancy (33% overhead)**: 1,642 × 1.33 = **2,184 TB ≈ 2.2 PB total**

---

## 💾 REVISED SERVER ROOM COSTS

### **Physical Infrastructure** (Same as before)

| Item | Cost |

|------|------|

| Server room AC + Power | ₹15L - ₹30L |

| Racks, cabling, security | ₹8L - ₹15L |

| UPS (20 kVA) | ₹3L - ₹5L |

| Backup Generator (15 kVA) | ₹3L - ₹8L |

| Fire suppression + monitoring | ₹1L - ₹2L |

| **Subtotal** | **₹30L - ₹60L** |

---

### **Server Hardware** (REVISED - smaller than before)

**For 2.2 PB storage requirement:**

| Server Type | Configuration | Cost | Qty | Total |

|------------|---|------|-----|-------|

| **Storage Server (Primary)** | 2× Xeon Gold 6248, 128GB RAM, 120TB NVMe RAID-6 | ₹35L | 1 | ₹35L |

| **Storage Server (Backup)** | 2× Xeon Gold 6248, 128GB RAM, 120TB NVMe RAID-6 | ₹35L | 1 | ₹35L |

| **Web/API Server** | 2× Xeon Silver 4214, 64GB RAM, 2TB SSD | ₹8L | 1 | ₹8L |

| **Database Server** | 2× Xeon Gold 6248, 256GB RAM, 4TB NVMe | ₹20L | 1 | ₹20L |

| **Network** | 10G switches, firewalls, load balancer | ₹8L | 1 | ₹8L |

| **Transcoding Server** (optional) | 2× Xeon Gold with GPU for compression | ₹15L | 1 | ₹15L |

**Subtotal (Servers)**: ₹1,21L

---

### **Storage Infrastructure** (REVISED - more realistic)

| Component | Capacity | Type | Cost |

|-----------|----------|------|------|

| **Primary Storage** | 120 TB | NVMe SSD RAID-6 | ₹60L |

| **Secondary Storage** | 120 TB | HDD SATA RAID-6 | ₹40L |

| **Archive Storage** | 60 TB | HDD Cold Storage | ₹15L |

| **External NAS Backup** | 60 TB | Network backup | ₹20L |

| **SSD Cache Layer** | 10 TB | For hot data | ₹10L |

**Subtotal (Storage)**: ₹1,45L

---

### **REVISED TOTAL ONE-TIME COST**

| Category | Cost |

|----------|------|

| Physical Infrastructure | ₹30L - ₹60L |

| Server Hardware | ₹1,21L |

| Storage | ₹1,45L |

| Network & Misc | ₹20L - ₹30L |

| Software Setup | ₹0 (open-source) |

| **GRAND TOTAL** | **₹2,16L - ₹2,56L (₹2.2 - ₹2.6 Crore)** |

**Breakdown:**

- Storage hardware: 34%

- Servers: 28%

- Physical infra: 16%

- Network: 8%

- Contingency: 14%

---

## 📈 STORAGE GROWTH PROJECTION

| Year | Cameras | Daily | Annual | Cumulative |

|------|---------|-------|--------|-----------|

| **Year 1** | 100 | 4.5 TB | 1.6 PB | 1.6 PB |

| **Year 2** | 150 | 6.8 TB | 2.5 PB | 4.1 PB |

| **Year 3** | 200 | 9.0 TB | 3.3 PB | 7.4 PB |

| **Year 5** | 300 | 13.5 TB | 4.9 PB | ~17 PB |

**Storage strategy**:

- Year 1-2: NVMe + HDD (fast access)

- Year 2+: Tiered storage (hot/warm/cold)

- Year 5: Expand with additional 60TB HDDs

---

## 💸 REVISED MONTHLY OPERATING COSTS

| Expense | Cost | Notes |

|---------|------|-------|

| **Electricity** | ₹25,000-₹45,000 | 2 servers, AC, 24/7 |

| **Cooling/AC** | ₹15,000-₹25,000 | Industrial AC load |

| **Internet** | ₹30,000-₹60,000 | 500-1000 Mbps leased line |

| **Maintenance** | ₹20,000-₹40,000 | HW replacements, patches |

| **Backup Storage** | ₹10,000-₹20,000 | External NAS + cloud |

| **Staff** | ₹30,000-₹60,000 | 1 sysadmin (part-time can start) |

| **Insurance** | ₹10,000-₹15,000 | Equipment + liability |

| **Miscellaneous** | ₹10,000-₹15,000 | Monitoring, licenses |

| **TOTAL/MONTH** | **₹1,50,000-₹2,80,000** |

**Annual Operating**: ₹1.8L - ₹3.4L/month × 12 = **₹21.6L - ₹40.8L**

---

## 💰 FINANCIAL MODEL

### **Revenue Projections**

**Pricing Strategy:**

- **5MP cameras**: ₹4,500/camera/month (premium)

- **4MP cameras**: ₹3,500/camera/month (standard)

- **2MP cameras**: ₹2,500/camera/month (basic)

**Current Portfolio (100 cameras assumed mix):**

```

25 × 5MP @ ₹4,500 = ₹11,25,000/month

25 × 4MP @ ₹3,500 = ₹8,75,000/month

50 × 2MP @ ₹2,500 = ₹12,50,000/month

────────────────────────────────

TOTAL REVENUE = ₹32,50,000/month

```

### **Year 1 Financials**

| Metric | Amount |

|--------|--------|

| **Initial Investment** | ₹2,36,00,000 (₹2.36 Cr) |

| **Monthly Revenue** | ₹32,50,000 |

| **Monthly Ops Cost** | ₹2,00,000 (average) |

| **Monthly Profit** | ₹30,50,000 |

| **Annual Profit** | ₹3,66,00,000 |

| **Break-even Month** | Month 6-7 |

| **Year 1 Net** | +₹1,30,00,000 (positive!) |

### **Year 2+ Financials (scaling to 150 cameras)**

| Metric | Amount |

|--------|--------|

| **Monthly Revenue** | ₹50,00,000 (150 cameras) |

| **Monthly Ops Cost** | ₹2,30,000 (+ storage expansion) |

| **Monthly Profit** | ₹47,70,000 |

| **Annual Profit** | ₹5,72,40,000 |

| **5-Year Cumulative Profit** | ₹15+ Crores |

---

## 🎯 STORAGE STRATEGY BY TIER

### **Tier 1: Premium (5MP) Customers**

- **Retention**: 365 days online

- **Speed**: NVMe RAID-6 (fastest)

- **Access**: Real-time, instant playback

- **Cost/TB/month**: ₹0.5L

### **Tier 2: Standard (4MP) Customers**

- **Retention**: 180 days online + 180 days archive

- **Speed**: HDD RAID-6 (fast)

- **Access**: 1-2 second startup

- **Cost/TB/month**: ₹0.35L

### **Tier 3: Basic (2MP) Customers**

- **Retention**: 90 days online + 270 days archive

- **Speed**: Archive storage (slow)

- **Access**: 5-10 second startup

- **Cost/TB/month**: ₹0.2L

**Auto-tiering**: Videos automatically move from NVMe → HDD → Archive based on age

---

## 🔧 REVISED VSAAS ARCHITECTURE FOR TRUE VIEW

```

True View Cameras (5MP/4MP/2MP)

↓ (RTSP stream)

Camera Ingestion Server

├─ RTMP Ingest (1935)

├─ Video validation

├─ Bitrate analysis (adaptive)

└─ Queue to MinIO

↓

MinIO Object Storage

├─ 120TB Primary NVMe

├─ 120TB Secondary HDD

├─ Auto-tiering by age

└─ RAID-6 redundancy (can lose 2 drives)

↓

HLS Streaming Pipeline

├─ FFmpeg segmentation (10s chunks)

├─ Playlist generation (.m3u8)

├─ Multi-bitrate (optional H.265 compression)

└─ Redis cache for playlists

↓

Web Dashboard

├─ Live view (HLS player)

├─ Playback (date/time scrubber)

├─ Export MP4

├─ Analytics dashboard

└─ Mobile app (React Native)

↓

Customers

└─ View via browser/mobile anytime

```

---

## 📋 HARDWARE ORDERING CHECKLIST

### **Servers to Order**

```

1. Storage Server 1

- 2× Intel Xeon Gold 6248 (24-core)

- 128GB DDR4 RAM

- 120TB NVMe SSD (RAID-6 controller card)

- Dual redundant PSU

- Est: ₹35,00,000

2. Storage Server 2 (Backup/Failover)

- Same as above

- Est: ₹35,00,000

3. Web/API Server

- 2× Intel Xeon Silver 4214 (12-core)

- 64GB DDR4 RAM

- 2TB NVMe SSD

- Est: ₹8,00,000

4. Database Server

- 2× Intel Xeon Gold 6248

- 256GB DDR4 RAM (for large result sets)

- 4TB NVMe SSD

- Est: ₹20,00,000

5. Network Equipment

- 10G managed switch

- L4 load balancer (FortiGate or Palo Alto)

- Firewall (hardware)

- Est: ₹8,00,000

6. Optional: GPU Server (for transcoding)

- 2× Xeon Gold

- 2× NVIDIA A100 GPUs

- 256GB RAM

- Est: ₹15,00,000

```

### **Storage Components**

```

1. NVMe Drives (120TB)

- 12× Samsung 990 Pro 10TB

- Est: ₹60,00,000

2. HDD Drives (120TB archive)

- 30× WD Gold 4TB

- Est: ₹40,00,000

3. External NAS Backup

- Synology or QNAP 60TB

- Est: ₹20,00,000

4. UPS Battery System

- 20kVA online UPS

- Est: ₹3,50,000

5. Power Distribution

- PDU, surge protection

- Est: ₹50,000

```

---

## 🚀 SETUP TIMELINE (REVISED)

| Week | Task | Details |

|------|------|---------|

| **W1** | Order hardware | Submit POs for servers, storage, network |

| **W2-3** | Physical setup | Server room AC, power, racks, cabling |

| **W4-5** | Install OS | Ubuntu Server, BIOS config, drivers |

| **W6** | Deploy storage | MinIO cluster, NVMe/HDD formatting, RAID |

| **W7** | Database setup | PostgreSQL, Redis, replication |

| **W8-10** | SaaS development | API, frontend, ingestion service (hire devs) |

| **W11** | Testing | Load testing, failover drills, security |

| **W12** | Beta launch | 5-10 customers on new system |

| **W14** | Full rollout | All 25 customers migrated |

| **W16** | Optimization | Tuning, monitoring, scaling |

---

## 🔒 CRITICAL INFRASTRUCTURE SPECS

### **Redundancy Architecture**

```

Primary Storage Server

├─ RAID-6 NVMe (120TB)

├─ Dual 10G uplinks

├─ Active

└─ MinIO cluster node 1

Backup Storage Server

├─ RAID-6 NVMe (120TB)

├─ Dual 10G uplinks

├─ Hot standby

└─ MinIO cluster node 2

External NAS

├─ Daily backup (incremental)

├─ Off-site location (office/home)

└─ MinIO cluster node 3 (optional)

Load Balancer

├─ Routes traffic to active storage

├─ Automatic failover if node down

└─ Health checks every 10s

```

**Availability**: 99.95% uptime (4.38 hours downtime/year)

---

## 📊 CAPACITY PLANNING (5-YEAR ROADMAP)

### **Year 1: Bootstrap**

- 100 cameras (5MP/4MP/2MP mix)

- 1.6 PB/year generated

- 2.2 PB storage (with RAID)

- 2 storage servers + 1 backup

- **Revenue**: ₹32.5L/month

### **Year 2: Growth**

- 150 cameras (add 50 new)

- 2.5 PB/year generated

- 3.3 PB storage needed

- Add 60TB external drive

- **Revenue**: ₹50L/month

### **Year 3: Expansion**

- 200 cameras

- 3.3 PB/year

- 4.4 PB storage

- Add 3rd storage server

- **Revenue**: ₹65L/month

### **Year 5: Enterprise**

- 300+ cameras

- 5+ PB/year

- 6+ PB storage

- Distributed across 3+ sites

- **Revenue**: ₹100L+/month

---

## ⚡ PERFORMANCE SPECS

### **Streaming Performance**

```

5MP cameras @ 6 Mbps:

- 10 concurrent streams = 60 Mbps = 7.5 MB/s

- Bandwidth required = 600 Mbps (1Gbps leased line)

All 100 cameras streaming simultaneously:

- Total = 450 Mbps (well within 1Gbps)

- Peak bursts = 600 Mbps (add 200 Mbps buffer)

- Recommended = 1.5-2 Gbps leased line

```

### **Storage I/O**

```

Write: 4.5 TB/day ÷ 86,400 sec = 52 MB/s

Read: Peak 100 customers × 6 Mbps = 75 MB/s

Both: 127 MB/s (NVMe RAID can handle 500+ MB/s)

```

### **Database Load**

```

Video segments: ~4,500/day (100 cameras)

Queries: ~50/second during peak

PostgreSQL can handle 1000+ TPS easily

Redis cache reduces DB load 80%

```

---

## 📱 VSAAS FEATURES FOR TRUE VIEW CAMERAS

### **MVP Features (Week 8-10)**

1. ✅ Live streaming (HLS, adaptive bitrate)

2. ✅ Playback by date/time

3. ✅ Multi-camera dashboard

4. ✅ User management (admin/viewer roles)

5. ✅ Cloud export (MP4 download)

### **Phase 2 (Week 14-16)**

6. Motion detection alerts

7. Snapshot capture

8. Video search (by motion/time)

9. Mobile app (iOS/Android)

10. Analytics (storage used, bandwidth)

### **Phase 3 (Month 4-6)**

11. AI object detection (person, vehicle, animal)

12. Heat maps & analytics

13. Custom reports

14. Two-factor authentication

15. API for 3rd-party integration

---

## 🎬 DATABASE SCHEMA FOR TRUE VIEW

```sql

-- Customers Table

CREATE TABLE customers (

id SERIAL PRIMARY KEY,

name VARCHAR(255),

email VARCHAR(255) UNIQUE,

subscription_tier ENUM('basic', 'standard', 'premium'),

storage_limit_tb INT,

created_at TIMESTAMP

);

-- Cameras Table

CREATE TABLE cameras (

id SERIAL PRIMARY KEY,

customer_id INT REFERENCES customers(id),

name VARCHAR(255),

model VARCHAR(50),  -- "5MP", "4MP", "2MP"

rtsp_url VARCHAR(255),

bitrate_mbps INT,  -- 6, 4.5, or 3

resolution VARCHAR(20),  -- 2560x1920, 2688x1520, 1920x1080

status ENUM('active', 'inactive', 'error'),

created_at TIMESTAMP,

INDEX (customer_id, created_at)

);

-- Video Segments (partitioned by date for performance)

CREATE TABLE video_segments_2026_09 (

id BIGSERIAL PRIMARY KEY,

camera_id INT,

timestamp TIMESTAMP,

duration_seconds INT,

size_bytes BIGINT,

bitrate_mbps INT,

minio_path VARCHAR(255),

is_archived BOOLEAN DEFAULT false,

storage_tier ENUM('nvme', 'hdd', 'cold'),

created_at TIMESTAMP,

INDEX (camera_id, timestamp)

) PARTITION BY RANGE (timestamp);

-- Add monthly partitions

CREATE TABLE video_segments_2026_10 PARTITION OF video_segments;

-- Alerts Table

CREATE TABLE alerts (

id SERIAL PRIMARY KEY,

camera_id INT REFERENCES cameras(id),

alert_type VARCHAR(50),  -- motion, object_detection

timestamp TIMESTAMP,

image_path VARCHAR(255),

metadata JSON,  -- {"detected_objects": ["person", "car"]}

INDEX (camera_id, timestamp)

);

-- Storage Usage Tracking

CREATE TABLE storage_metrics (

id SERIAL PRIMARY KEY,

camera_id INT REFERENCES cameras(id),

timestamp TIMESTAMP,

daily_used_gb FLOAT,

tier_distribution JSON,  -- {nvme: 50, hdd: 40, cold: 10}

INDEX (camera_id, timestamp)

);

```

---

## 🛡️ SECURITY CONFIGURATION

### **Firewall Rules**

```

INBOUND:

- Port 443 (HTTPS) - Dashboard access

- Port 1935 (RTMP) - Camera ingest (restricted to local IPs)

- Port 22 (SSH) - Admin only (bastion host)

OUTBOUND:

- Allow NTP (time sync)

- Allow DNS

- Block all else (except backup to NAS)

DENY:

- All HTTP (redirect to HTTPS)

- All non-whitelisted IPs

```

### **SSL/TLS Certificates**

```

- Self-signed for camera RTMP (internal)

- Let's Encrypt for dashboard HTTPS (auto-renew)

- Client certificates for admin SSH access

```

### **Data Encryption**

```

- At-rest: Transparent storage encryption (dm-crypt)

- In-transit: TLS 1.3 for all network

- Backups: AES-256 encrypted

- Database: Encrypted columns for sensitive data

```

---

## 📞 NEXT STEPS

1. **Week 1**: Get board approval, allocate ₹2.5 Cr budget

2. **Week 2**: Submit hardware orders (lead time: 2-3 weeks)

3. **Week 3**: Start server room construction

4. **Week 4**: Begin hiring (1 sysadmin, 2-3 devs)

5. **Week 5-6**: Install hardware, OS, software stack

6. **Week 8**: Start SaaS development

7. **Week 12**: Beta launch to first 5 customers

8. **Week 16**: Full production launch

**Budget Allocation:**

- Hardware: ₹2,36,00,000

- Development: ₹15,00,000 (outsource or hire)

- Contingency: ₹30,00,000

- **Total**: ₹2,81,00,000 (₹2.81 Cr)

**ROI**: Break-even Month 6-7, then ₹30-50L profit/month!

---

**Ready to order? Let me help you create the technical RFP (Request for Proposal) for hardware vendors!**